## Sheet1
Designer's Risk Register (DRR)
Register Reference
Project NeRV Centre
Package/Topic | [6 empty] | Post-construction / Completion
Remember: Avoid – Reduce – Control and Communicate relevant information to others
Item | Discipline | Area/Location of Risk Exposure | Description of Hazard and Risk Exposure | Mitigation of Risk (Potential or Achieved) | A | R | C | Further Action | By | Status Active / Closed
1 | CDM | Demo Facility - interface | Site boundaries / liaison and interfaces | Site boundaries, roles and responsibilities to be clearly defined to ensure H&S issues are clear and coordinated with regular liaison / communication |  |  | C | Strategic management plan and arrangements to manage the project H&S aspects with clear definition of CDM roles | NGN | Active
2 | CDM | Demo Facility - interface | Sharing of design / H&S information | H&S risks to be communicated / shared with adjacent projects / interfaces |  |  | C | PCI / DRR to be shared between interfacing projects. PCI shared with Client for issue to relevant parties. | NGN | Active
3 | CDM | Information | Relevant information to inform and enable design and management of H&S risks | Lack of relevant information may lead to the potential for utility strikes, inappropriate design assumptions etc. |  |  | C | PCI document to collate available information and identify any gaps relevant to the next stage of design PCI document prepared and shared. | NGN | Active
4 | Hydrogen | NeRV site wide and in Buildings | Risk that escaped hydrogen may ignite resulting in invisible flame causing a hazard and damaging equipment and potentially leading to explosion | Potential use of an odouriser being introduced into the hydrogen so it is detectable if there is a leak, or other means of monitoring e.g. low pressure alarms, hydrogen monitors, flame / heat detection sensors etc.. |  | R | C | NGN to review and consider if additional hydrogen safety measures are to be adopted in addition to the current safety measures and monitoring devices incorprated into the design. | NGN | Active
5 | Hydrogen | Site wide | Risk that local fire & rescue crews will be unfamiliar with dealing with hydrogen emergencies resulting in incorrect procedures being used on a potential fire | Local Fire crews should have H2 training |  |  | C | NGN to liaise with local fire and rescue crews informing them of the risks on site. Emergency Response Plan to be reviewed and updated on a regular basis. | NGN | Active
6 | CDM | Site wide | Live traffic, operational and construction activities within the wider NGN site. | Traffic management plan to be implemented. Weekly working diaries to the provided to NGN to coordinate with wider works. |  | R | C | PC to prepare a traffic management plan. Project Diaries | NGN | Active
7 | Utilities | Site wide | Risk of unrecorded or incorrectly recorded utility locations. Injury from striking buried services. | Acquisition and review of service information as part of the Design. |  | R | C | NGN should be aware of the possibility of unrecorded utilities being present within the NeRV site and the possibility of inaccuracies in the as built locations of utilities. NGN should operate appropriate safety measures during any future earthworks in the vicinity of the site. | NGN | Active
8 | Utilities | Site wide | Proximity to HP gas main - gas escape / explosion | Contractor to adopt safe method of work, assess risk of vibration and undertake work in accordance with related gas safety regulations and guidance |  | R | C | NGN to control risk during any future works within the NeRV site. | NGN | Active
9 | Utilities | Site wide | Works located about position of gas pipelines. Potential for gas strikes during excavation works on site. | Consultation with NGN for service information and liaison for protocol during construction works. |  | R | C | Site contractor to review utility drawings for adequacy before site works. Appropriate site safety measures should be undertaken before excavation can begin. | NGN | Active
10 | Utilities | Site wide | Working with electricity - Death or serious injury from potential Electric Shock. | Electrical installation work to be carried out only by qualified electricians. Electrical testing to be undertaken by competent personnel. Full Isolation to be carried out before commencing any works. Operatives to be G39 trained. |  | R | C | Full Isolation is to be carried out on all circuits. Work to be undertaken using suitable insulated tools and suitable PPE to be worn. NGN to ensure all works to electrical networks required under future testing requirements should be undertaken by a qualified person and following safe working guidance. | NGN | Active
11 | Drainage | Site wide | Exposure to waterborne bacteria and diseases such as Weil’s Disease. Working in/on existing surface water sewers. | Ensure personnel are vaccinated where appropriate. Suitable personal protective equipment and adopt approriate hygiene measures. |  |  | C | NGN to provide suitable safeguarding measures for personnel accessing and emptying the Cesspit and Interceptor and any maintenace to the drainage networks. | NGN | Active
12 | Drainage | Drainage Tanks - cess pit and interceptor | Working in confined spaces risk of asphyxiation | Proposed design minimises the need for entry into the tank. The O&M for the tanks identifies potential hazards and associated risk with inspection, cleaning and maintenance activities. |  | R | C | Specialist licenced contractor and safe system of work to be used for inspection, maintenance, emptying and cleaning activities. This work should be in accordance with the O&M manual provided by the designer / installer and the H&S File. | NGN | Active
13 | Highways | NeRV Site | Tar bound material (a hazardous, special waste) discovered as being present in excavated materials | If the spoil show that tar bound materials are present, special care should be taken to reuse, recycle, or dispose of it in a suitable manner. |  |  | C | Waste management plan | NGN | Active
14 | Highways | NeRV Site | Potential for contamination to be present associated with made ground. | Scheme specific ground investigation undertaken including contamination testing and a contamination risk assessment. |  |  | C | Contractor to adopt appropriate health and safety and environmental protection measures during the earthwork’s phases of the project. This should include appropriate PPE, hygiene measures, dust control, sheeting of vehicles, good site housekeeping and confined spaces best practice. Contractor to carry out inspection of all excavations for evidence of contamination, with appropriate testing and assessment to identify the scope of any remedial measures or additional health and safety controls that may be necessary. Should any evidence of asbestos in soils be identified, specialist advice will need to be sought to assess and mitigate potential risks in line with the requirements of the Control of Asbestos Regulations 2012 (CAR,2012). | NGN | Active
15 | Geo | NeRV Site | Potential for mine workings | Preliminary Coal Mining Risk Assessment undertaken by Atkins (December 2020) |  |  | C |  | NGN | Active
16 | Geo | NeRV Site | Potential for asbestos containing/ contaminated materials within made ground materials previously placed on the site - health issue for personnel | Where applicable, management of asbestos to be controlled in accordance with Control of Asbestos Regulations and HSE guidance. Contractor to notify the Client for asbestos register / H&S File. |  |  | C | Contractor to confirm if any presence of asbestos/ contamination was encountered during the works. Any asbestos encountered to be recorded in the site asbestos register / H&S File. Any contamination to be recorded within the H&S File | NGN | Active
17 | Geo | NeRV Site | Buried obstructions leading to delays during construction, hard spots and differential settlement of buildings. | Potential for obstructions mitigated through ground investigation and removal of obstructions during construction |  |  | C |  | NGN | Active
18 | Geo | Site wide | Working in the vicinity of embankments and steep gradients. Risk of personnel, equipment falls and overturning plant. | Design has plateaued out the NeRV site levels |  |  | C | Contractor to provide method statement prior to any dismantling or installation work is undertaken Satisfying the requirements of CDM Regulation. | NGN | Active
19 | Drainage | Site wide | High rate of overland flow | Design to include cut of drainage to the north of the development to convey overland flow from the PV farm away from NeRV and into the existing drainage system. |  | R |  | Contractor to provide construction phase drainage plan and operate safe methods of working. | NGN | Active
20 | Environmental |  | Potential for non-invasive species and protected species on site. |  |  |  | C | Contractor to be made aware. | NGN | Active
21 | Environmental |  | Potential for wildlife on site. Deer spotted on site | Contractor to ensure all excavations are kept safe. |  |  | C | Contractor to implement appropriate procedures to minimise impact or disturbance. | NGN | Active
22 | M&E | Loose control cabling and trip hazards | Control equipment in the dwellings (eg acutators to open doors, windows etc) will be surface cabled. Risk of people tripping on cables | Require contractor to install anti-trip mats and use conduit where necessary | ✓ |  | C | Clauses in specification | NGN | Active
23 | Geo | Site wide | Potential for Hydrocarbons within the ground | Gas monitoring caried out as part of GI. |  |  | C | Contractor to ensure all excavations are kept safe. Contractor to adopt appropriate health and safety and environmental protection measures during the earthwork’s phases of the project | NGN | Active
24 | Geo | Site wide | Water levels monitored within the GI. Potential for localised perched water. | Water levels monitored within the GI. |  |  | C | Contractor to ensure all excavations are kept safe. Posible need for localised dewatering. Contractor to adopt appropriate health and safety and environmental protection measures during the earthwork’s phases of the project. | NGN | Active
25 | Civils / Structural | Site wide | Excavation Stability. The existing site has mixed fill and historical foundations. Excavation faces for new foundations may be unstable due to this and could require temporary shoring/benching during site works | Contractor to allow for temporary shoring of excavations |  |  | C | Highlight need for Contractor to consider temporary excavation stability on foundation sketches. | NGN | Active
26 | Civils / Structural | Site wide | Demolition of unknown materials. No as built information available on site. Possible demolition required of a retaining structure. All existing slabs and hardstanding to be removed. | Scheme specific ground investigation including core samples and contamination testing and a contamination risk assessment. |  |  | C | Contractor to adopt appropriate health and safety and environmental protection measures during demolition. This should include appropriate PPE, hygiene measures, dust control, sheeting of vehicles, good site housekeeping and confined spaces best practice. Contractor to carry out inspection of all elements to be demolitioed. If the demolition materials show that contaminants are present, special care should be taken to reuse, recycle, or dispose of it in a suitable manner. | NGN | Active
27 | Civils / Structural | Retaining Wall | Potential falls from height from the retaining wall. | A fence to protect against falls from height in this location. | ✓ |  |  | Contractor to tprovide emporary works to protect workers from falling during the construction works | NGN | Active
28 | Structural | All plots / buildings | Potential for structural elements to be hidden by finishes. Potential for inadvertent damage to structural building elements that are loading bearing and/or provide structural stability and integrity by unconctrolled alterations or amendments. | O&M manual /H&S File to make clear that no structural alterations are to take place without referring to the structural drawings and consulting a suitably qualified structural engineer. |  |  | C | O&M manual / H&S File to be circuated as appropriate to those responsible for future design work including amendments, alteration, extension or new works + the principal contractor / contractors if construction works proceed or maintenec being undertaken. | NGN | Active
29 | Utilities | External works (underground) - Whole NeRV site and the wider site | Location of all underground services to to be confirmed and As-Built Drawings prepared. Potential for utility strike and injury to personnel. Loss of services to critical buildings / plant. Escape of gas / explosion. | External services to be surveyed, locations surveyed and recorded on as-built drawings. Trial pit investigation may be required. Review provision of marker posts / plates etc.. |  | R | C | Client to ensure that As-Built records are provided /prepared and included in the Health & Safety File (HSF). HSF to be provided to to all future Designers, PD , PC and Contractors undertaking design or construction work including maintenance. | NGN | Active